ELG4125

Case Study 3:Electric Power Transmission, Distribution & Utilization

Kareim EL Attar, 6221386

Professor: Riadh Habash

12/10/2013

- Power system block diagram

- Design specifications of power plant

The Itaipu HVDC in Brazil:

| Variables/Specifications | Value |
| --- | --- |
| Speed | 92.3 rpm |
| Power Output | 20 x 700 MW |
| Volt-Amps | 737 MVA |
| Frequency | 60 Hz |
| Poles | 2 x bi-poles |
| Type of turbine | Francis |
| Poles rating | 3,150 MW |

**A hydroelectric generator was used to match the criteria given for us in the question.

- Transmission Line & Conductor:

Guyed cross-rope: Cost is a key factor as well as weight, hence the Guyed cross-rope seems like the ideal transmission tower. With a voltage range of 230 – 735 kV, and an average weight of 5000 kg, it suits our criteria well.

ACSR conductor – Finch

| Specifications | Value |
| --- | --- |
| Current capacity | 1110 A |
| Weight | 7544 lbs./miles |
| Inductance | 0.380 Ω |
| Reactance | 0.0969 Ω |
| Shunt capacitance | 0.867 x 106 F |
| Number of strands | 54 |
| Strength | 40200 lbs. |

- Numbers of conductors/bundle: 3 (bundles are used to have low electric field strength at the conductor surface)

- 3-phase conductors

- 4 number of strings per phase

- 450 mm sub conductor spacing

- Calculations

| Parameter | Equation | Value |
| --- | --- | --- |
| A | Z.Y2+1 | 0.86∠2.1° |
| B | Z | 313.4∠77.5° |
| C | Z.Y4+1 | 8.64 ×10-4∠91° |
| D | A | 0.86∠2.1° |

Where, 
z=R+jL=0.134+j0.612 Ω/km

And
y= 1C=1.86 ×10-6∠90°

To find Z and Y, we multiply the above values by the total distance (500 Km)

Z=313.4∠77.5°  &  Y=0.00093∠90°

Using the matrix

Therefore

Vr=D.Vs-B.IsD.A-B.C=497 kV

Ir=Is-C.VrD=1775 A

Using the equation
%Power Efficiency=Vr×IrVs×Is=98 %

- Substations

Which? ACSR conductor – Eagle

| Specifications | Value |
| --- | --- |
| Current capacity | 730 A |
| Weight | 4588 lbs./miles |
| Inductance | 0.415 Ω |
| Resistance | 0.1859 Ω |
| Capacitive reactance | 0.0957 Ω |
| Number of strands | 30 |
| Conductors/Bundle | 1 |

Calculations?

| Parameter | Value |
| --- | --- |
| Z | 28.88 + j64.47 Ω |
| Y | j0.0016 S |
| A | 0.95+j0.02 |
| B | 28.88 + j64.47 Ω |
| C | -0.000018+j0.0016 |
| D | 0.95+j0.02 |
| Vs | 591 6.97 |
| Is | 1894 26 |

Primary and secondary of the distribution system utilize either the Wye-connected 3-phase circuits with multi-grounded neutrals, or the Center tapped single-phase circuits with multi-grounded neutrals. For this report we will focus on the center tapped single-phase circuit.

- Protection

For general power system configurations, a fundamental concept is the division of a system into protective zones. If a fault occurs anywhere in a zone, action will be taken to isolate that zone from the rest of the system.

- Generator Protection:

| Generator Fault: | Stator Faults: | Protection against both |
| --- | --- | --- |
| - Winding faults | - Phase to earth faults | - Differential Protection |
| - Field winding/Rotor | - Phase to phase faults | - Stator inter-turn protection |
| Circuit Faults | - Inter-turn faults |  |

- Bus Protection:

| Area | Type of Protection(Relays) | Rating: (V) Voltage Ratio | Rating: (A) Current Ratio |
| --- | --- | --- | --- |
| Buses | Differential Relays | 3000 : 1 | 1000 : 5 |

- Transformer Protection:- Differential Relays are used.

- Transmission Line Protection:

| Area | Type of Protection(Relays) | Rating: (V) Voltage Ratio | Rating: (A) Current Ratio |
| --- | --- | --- | --- |
| Transmission Line | Impedance Relays | 3000 : 1 | 1000 : 5 |

- Sizing Transformers

- 1st current & voltage sizing

| Variable | Equation + Result | Ratio |
| --- | --- | --- |
| MVA Output | (500 kV)*(900 A)= 450 MVA | 4:1 |
| IRATED(PRIMARY) | 450×106500×1000×3=519A | 600:5. |
| IRATED(SECONDARY) | 450×106491×1000×3=529A | 600:5. |
| I1 | 519×5600=4.3 A | ____ |
| I2 | 529×5600=4.4 A | ____ |

- 2nd  current & voltage sizing

| Variable | Equation + Result | Ratio |
| --- | --- | --- |
| MVA Output | (500 kV)*(900 A)= 450 MVA | 4:1 |
| IRATED(PRIMARY) | 450×106491×1000×3=529A | 600:5. |
| IRATED(SECONDARY) | 450×106480×1000×3=541A | 600:5. |

- Circuit Breaker sizing

12500.8*125100=195.3 kA

- Distribution System:

Specifications for distribution substation system

| Variable | Comment/Data |
| --- | --- |
| Medium voltage Vegeta distribution transformer | 25 MVA |
| Conversion for sub transmission | 69 kV – 13.8 kV |
| Rated Power | 50 kVA – 25 MVA |
| Rated insulation level | Up to 72.5 kV |
| Rated Frequency | 60 Hz |
| Insulating liquid | Natural Ester |
| High fire point insulating liquid of K-class |  |
| Protection | Neutral grounding |
| Hermetically sealed with conservator conventional |  |
| Topology used | Loop topology – high service reliability & good for commercial use |

| Protection devices | Specifications | Comment |
| --- | --- | --- |
| Circuit Breaker (14.4 Nominal KV) | Rated Max KV; 15.5. Rated Voltage; 1 V. Rated Current; 1200 A. | Type: SPS2-15.5-31.5 |
| Fuse (20 MVA) | Rated Max KV; 20. Max Current; 1000 A. | Type: Electronically controlled VSO |
| Recloser (25 MVA) | Rated Current; 1000 A. Max Voltage; 27 kV. | Type: CMU702003 |